## README
WWTP Model Input Template — SUMO24 MCP
Section | Description
Purpose | Fill this workbook with the available data for your wastewater treatment plant. The SUMO24 MCP server can read it with `read_wwtp_template`, validate it with `validate_wwtp_template`, and build a SUMO24 model from scratch with `build_model_from_template`.
Workflow | 1) Plant_Info 2) Influent_Dataset & Influent_Fractionation 3) Effluent_Dataset & Effluent_Targets 4) Treatment_Processes 5) Connections 6) Process_Sizing 7) Bio/Phys/Chem_Operational 8) Save and call `build_model_from_template`.
Cell colour key | Navy header rows are not editable. Pale-blue cells are user inputs. Gray cells contain unit hints. Yellow cells are notes.
Required vs optional | Plant_Info, Treatment_Processes and Connections are required. Other sheets are optional but improve calibration quality.
Time-series sheets | Influent_Dataset and Effluent_Dataset accept daily or sub-daily timestamps (yyyy-mm-dd or yyyy-mm-dd HH:MM). Missing values may be left blank.
Variable_Map | Reference sheet listing the SUMO state variables that map to each column.
Tip — units | Concentrations in mg/L; flows in m3/d; T in degC; volumes in m3; areas in m2; alkalinity in mmol/L.
Tip — order matters | Treatment_Processes.order_index controls the topological order in which units are added — keep Influent first, Effluent last.
Egyptian context | Effluent_Targets is preloaded with Law 48/1982 default limits.

## Plant_Info
1. Plant Information
Field | Value | Unit | Description / hint
project_name | MyPlant_2026 | - | Identifier used for the .sumo file and folder name.
project_path | F:/UNI/SUMO/MCP/projects | - | Absolute folder where the project will be created.
plant_location |  | - | City, country, or coordinates.
design_flow_avg |  | m3/d | Average dry-weather design flow.
design_flow_peak |  | m3/d | Peak hourly design flow.
design_flow_min |  | m3/d | Minimum night-time flow.
design_population |  | PE | Design population equivalent.
kinetic_model | ASM2d | - | ASM1 / ASM2d / ASM3 / ASM3+BioP / Mantis2.
temperature_design | 20 | degC | Reference design temperature.
temperature_min |  | degC | Coldest expected temperature.
temperature_max |  | degC | Hottest expected temperature.
elevation |  | m a.s.l. | Plant elevation.
discharge_target | law48_drain | - | law48_nile / law48_drain / custom.
project_currency | EGP | - | Reporting currency for OPEX/CAPEX.
created_by |  | - | Engineer or modeller name.
created_date |  | yyyy-mm-dd | Date of template completion.

## Influent_Dataset
2. Influent Dataset (time series)
Date | Q | COD | sCOD | BOD5 | TSS | VSS | TKN | NH4-N | NO3-N | TP | PO4-P | Alkalinity | pH | Temperature
yyyy-mm-dd | m3/d | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mmol/L | - | degC
Note on A3: Daily timestamp; sub-daily allowed.
Note on B3: Influent flow rate.
Note on C3: Total chemical oxygen demand.
Note on D3: Soluble (filtered) COD.
Note on E3: 5-day biochemical oxygen demand.
Note on F3: Total suspended solids.
Note on G3: Volatile suspended solids.
Note on H3: Total Kjeldahl nitrogen.
Note on I3: Ammonia nitrogen.
Note on J3: Nitrate nitrogen.
Note on K3: Total phosphorus.
Note on L3: Ortho-phosphate phosphorus.
Note on M3: Bicarbonate alkalinity.
Note on N3: pH (use median if range).
Note on O3: Influent temperature.

## Effluent_Dataset
4. Effluent Dataset (time series)
Date | Q | COD | sCOD | BOD5 | TSS | VSS | TKN | NH4-N | NO3-N | TP | PO4-P | Alkalinity | pH | Temperature
yyyy-mm-dd | m3/d | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mmol/L | - | degC
Note on A3: Daily timestamp; sub-daily allowed.
Note on B3: Influent flow rate.
Note on C3: Total chemical oxygen demand.
Note on D3: Soluble (filtered) COD.
Note on E3: 5-day biochemical oxygen demand.
Note on F3: Total suspended solids.
Note on G3: Volatile suspended solids.
Note on H3: Total Kjeldahl nitrogen.
Note on I3: Ammonia nitrogen.
Note on J3: Nitrate nitrogen.
Note on K3: Total phosphorus.
Note on L3: Ortho-phosphate phosphorus.
Note on M3: Bicarbonate alkalinity.
Note on N3: pH (use median if range).
Note on O3: Influent temperature.

## Influent_Fractionation
3. Influent COD/N/P Fractionation
Fraction | Value | Unit | Description
fSI | 0.07 | g COD/g COD | Soluble inert (SI) fraction of total COD.
fSS | 0.2 | g COD/g COD | Readily biodegradable (SS) fraction.
fXS | 0.5 | g COD/g COD | Slowly biodegradable (XS) fraction.
fXI | 0.15 | g COD/g COD | Particulate inert (XI) fraction.
fXBH | 0.08 | g COD/g COD | Heterotrophic biomass fraction.
fXBA | 0 | g COD/g COD | Autotrophic biomass fraction.
fSNH4 | 0.65 | g N/g TKN | Ammonia (NH4) fraction of TKN.
fSND | 0.1 | g N/g TKN | Soluble biodegradable organic N.
fXND | 0.18 | g N/g TKN | Particulate biodegradable organic N.
fSI_N | 0.02 | g N/g COD | Soluble inert N content.
fXI_N | 0.05 | g N/g COD | Particulate inert N content.
fSPO4 | 0.5 | g P/g TP | Ortho-phosphate fraction of TP.
fXPP | 0 | g P/g TP | Poly-phosphate fraction (PAOs).
fSI_P | 0.005 | g P/g COD | Soluble inert P content.
fXI_P | 0.01 | g P/g COD | Particulate inert P content.
Sum (fSI+fSS+fXS+fXI+fXBH+fXBA) |  | should ≈ 1.0 | If far from 1.0, revisit fractionation.

## Effluent_Targets
5. Effluent Discharge Targets / Permit Limits
Parameter | Limit | Unit | Stat | Source / notes
BOD5 | 60 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
COD | 80 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
TSS | 50 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
NH4-N | 5 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
TN | 50 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
TP | 3 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
Oil | 10 | mg/L | max | Egyptian Law 48/1982 — agricultural drains.
FC | 5000 | MPN/100mL | max | Faecal coliforms — agricultural reuse.
pH_min | 6 | - | min | Egyptian Law 48/1982.
pH_max | 9 | - | max | Egyptian Law 48/1982.

## Treatment_Processes
6. Treatment Processes (physical / biological / chemical)
order_index | instance_name | process_type | category | stage | kinetic_model | notes
1 | Influent | Influent | physical | headworks |  | Raw wastewater inflow.
2 | Screen1 | Screen | physical | headworks |  | Bar screen, 6 mm spacing.
3 | GritChamber1 | GritChamber | physical | headworks |  | Aerated grit chamber.
4 | PrimaryClarifier1 | PrimaryClarifier | physical | primary |  | Circular primary clarifier.
5 | AnaerobicTank1 | AnaerobicReactor | biological | biological | ASM2d | Selector / anaerobic zone for EBPR.
6 | AnoxicTank1 | AnoxicReactor | biological | biological | ASM2d | Pre-denitrification.
7 | AerationTank1 | AerationTank | biological | biological | ASM2d | Plug-flow aeration tank.
8 | SecondaryClarifier1 | SecondaryClarifier | physical | secondary | Takacs | Circular Takacs clarifier.
9 | TertiaryFilter1 | SandFilter | physical | tertiary |  | Optional tertiary filtration.
10 | DisinfectionUnit1 | UVDisinfection | physical | tertiary |  | UV disinfection.
11 | ChemDoser_FeCl3 | ChemicalDoser | chemical | secondary |  | FeCl3 dose for P precipitation.
12 | Thickener1 | GravityThickener | physical | sludge |  | WAS thickening.
13 | Digester1 | AnaerobicDigester | biological | sludge | ADM1 | Mesophilic anaerobic digester.
14 | Dewatering1 | Centrifuge | physical | sludge |  | Sludge dewatering.
15 | Effluent | Effluent | physical | effluent |  | Treated effluent discharge.

## Connections
7. Stream Connections (process network)
from_unit | to_unit | stream_name | stream_type | recycle_type | notes
Influent | Screen1 | S_inf_screen | liquid |  | Raw → screening.
Screen1 | GritChamber1 | S_screen_grit | liquid |  | Screened → grit.
GritChamber1 | PrimaryClarifier1 | S_grit_prim | liquid |  | Grit-removed → primary.
PrimaryClarifier1 | AnaerobicTank1 | S_prim_ana | liquid |  | Primary effluent → anaerobic.
AnaerobicTank1 | AnoxicTank1 | S_ana_anox | liquid |  | Anaerobic → anoxic.
AnoxicTank1 | AerationTank1 | S_anox_aer | liquid |  | Anoxic → aeration.
AerationTank1 | SecondaryClarifier1 | S_aer_sec | liquid |  | Aeration → secondary clarifier.
SecondaryClarifier1 | TertiaryFilter1 | S_sec_tert | liquid |  | Clarified → tertiary.
TertiaryFilter1 | DisinfectionUnit1 | S_tert_disinf | liquid |  | Tertiary → UV.
DisinfectionUnit1 | Effluent | S_disinf_eff | liquid |  | UV → effluent.
AerationTank1 | AnoxicTank1 | S_IR | recycle | InternalRecycle | Internal nitrate recycle.
SecondaryClarifier1 | AnoxicTank1 | S_RAS | recycle | RAS | Return activated sludge.
SecondaryClarifier1 | Thickener1 | S_WAS | recycle | WAS | Waste activated sludge.
PrimaryClarifier1 | Digester1 | S_PSL | sludge |  | Primary sludge → digester.
Thickener1 | Digester1 | S_TWAS | sludge |  | Thickened WAS → digester.
Digester1 | Dewatering1 | S_DigOut | sludge |  | Digested sludge → centrifuge.
Dewatering1 | AerationTank1 | S_Reject | recycle | RejectWater | Centrate back to aeration.
ChemDoser_FeCl3 | AerationTank1 | S_FeCl3 | liquid |  | FeCl3 dose into aeration tank.

## Process_Sizing
8. Process Sizing (per unit)
instance_name | n_units | volume_m3 | depth_m | surface_area_m2 | diameter_m | length_m | width_m | HRT_h | notes
Screen1 | 1 | [7 empty] | Mechanical bar screen.
GritChamber1 | 1 | 50 | 2 |  |  |  |  | 1 | Aerated grit chamber.
PrimaryClarifier1 | 1 | 800 | 3.5 | 230 | 17 |  |  | 2 | Circular primary clarifier.
AnaerobicTank1 | 1 | 600 | 4 |  |  | 25 | 6 | 0.6 | Anaerobic selector.
AnoxicTank1 | 1 | 1200 | 4 |  |  | 30 | 10 | 1.2 | Pre-denitrification.
AerationTank1 | 2 | 4000 | 4.5 |  |  | 40 | 22 | 6 | Two parallel aeration tanks.
SecondaryClarifier1 | 2 | 1500 | 4 | 380 | 22 |  |  | 3.5 | Two circular Takacs clarifiers.
TertiaryFilter1 | 2 |  |  | 60 |  |  |  |  | Sand / dual-media filters.
DisinfectionUnit1 | 1 | 50 | 1.5 | 30 |  | 10 | 3 | 0.2 | UV channel.
Thickener1 | 1 | 200 | 3 | 70 |  |  |  | 6 | Gravity thickener.
Digester1 | 1 | 3000 | 8 |  |  |  |  | 480 | Mesophilic digester (HRT in hours).
Dewatering1 | 1 | [7 empty] | Centrifuge — flow basis only.

## Bio_Operational
9. Biological-Process Operational Parameters
instance_name | parameter | value | unit | applies_to | notes
AerationTank1 | DO_setpoint | 2 | mg/L | aeration | DO setpoint.
AerationTank1 | kLa |  | 1/h | aeration | Override automatic kLa.
AerationTank1 | MLSS_target | 3500 | mg/L | aeration | Target MLSS.
AerationTank1 | SRT_target | 12 | d | aeration | Target solids retention time.
AerationTank1 | F_M_target | 0.2 | kgBOD/(kgMLVSS·d) | aeration | F:M ratio.
AerationTank1 | Temperature_op | 22 | degC | aeration | Operating temperature.
AnoxicTank1 | Mixing_power | 6 | W/m3 | anoxic | Mechanical mixing power.
AnoxicTank1 | DO_max | 0.2 | mg/L | anoxic | Maximum DO.
AnaerobicTank1 | Mixing_power | 6 | W/m3 | anaerobic | Mechanical mixing power.
AnaerobicTank1 | DO_max | 0.05 | mg/L | anaerobic | Strict anaerobic ceiling.
SecondaryClarifier1 | RAS_ratio | 0.75 | - | RAS | Q_RAS / Q_inf.
SecondaryClarifier1 | WAS_ratio | 0.02 | - | WAS | Q_WAS / Q_inf.
AnoxicTank1 | Internal_recycle_ratio | 3 | - | IR | Q_IR / Q_inf.
Digester1 | Temperature_op | 35 | degC | anaerobic | Mesophilic T.
Digester1 | HRT | 20 | d | anaerobic | Hydraulic retention time.
Digester1 | VS_loading | 2 | kgVS/(m3·d) | anaerobic | Volatile-solids loading.

## Phys_Operational
10. Physical-Process Operational Parameters
instance_name | parameter | value | unit | applies_to | notes
Screen1 | bar_spacing | 6 | mm | screen | Bar spacing.
Screen1 | approach_velocity | 0.6 | m/s | screen | At peak.
GritChamber1 | HRT | 3 | min | grit | At peak flow.
GritChamber1 | air_supply | 0.3 | m3/(m·min) | grit | Air per metre length.
PrimaryClarifier1 | SOR_avg | 32 | m3/(m2·d) | clarifier | SOR @ average flow.
PrimaryClarifier1 | SOR_peak | 80 | m3/(m2·d) | clarifier | SOR @ peak.
PrimaryClarifier1 | weir_loading | 125 | m3/(m·d) | clarifier | Weir overflow.
SecondaryClarifier1 | SLR_avg | 4 | kg/(m2·h) | clarifier | Solids loading.
SecondaryClarifier1 | SOR_avg | 24 | m3/(m2·d) | clarifier | SOR.
TertiaryFilter1 | filtration_rate | 8 | m/h | filter | Loading rate.
TertiaryFilter1 | backwash_rate | 30 | m/h | filter | Backwash.
DisinfectionUnit1 | UV_dose | 40 | mJ/cm2 | disinfection | At peak.
Thickener1 | SLR | 90 | kg/(m2·d) | thickener | Solids loading rate.
Dewatering1 | polymer_dose | 8 | g/kgDS | dewatering | Cationic polymer.
Dewatering1 | cake_solids_target | 22 | %TS | dewatering | Target cake DS.

## Chem_Operational
11. Chemical Dosing
instance_name | chemical | dose | unit | target_unit | purpose
ChemDoser_FeCl3 | FeCl3 | 50 | mg/L | AerationTank1 | Phosphorus precipitation.
| Alum |  | mg/L |  | Coagulation / P removal.
| PACl |  | mg/L |  | Coagulation / P removal.
| Polymer |  | mg/L |  | Flocculation aid.
| NaOH |  | mg/L |  | Alkalinity / pH adjustment.
| Ca(OH)2 |  | mg/L |  | pH / disinfection.
| Methanol |  | mg/L |  | External carbon for denitrification.
| Acetate |  | mg/L |  | External carbon.
| Cl2 |  | mg/L |  | Disinfection.
| NaOCl |  | mg/L |  | Disinfection.

## Variable_Map
12. Variable Map (column → SUMO state variable)
Column header | SUMO state var | Unit | Notes
Q | Q | m3/d | Volumetric flow rate.
COD | TCOD | mg/L | Total COD.
sCOD | SCOD | mg/L | Soluble COD (SI + SS).
BOD5 | BOD5 | mg/L | BOD5; computed from COD if absent.
TSS | TSS | mg/L | Total suspended solids.
VSS | VSS | mg/L | Volatile suspended solids.
TKN | TKN | mg/L | Total Kjeldahl nitrogen.
NH4-N | SNH | mg/L | Ammonia.
NO3-N | SNO | mg/L | Nitrate + nitrite.
TP | TP | mg/L | Total phosphorus.
PO4-P | SPO | mg/L | Ortho-phosphate.
Alkalinity | SALK | mmol/L | Bicarbonate alkalinity.
pH | PH | - | pH (informational only).
Temperature | T | degC | Bulk-liquid temperature.