## Help
DynaSand
Custom
DynaSand continuous up-flow sand filter (Type A custom unit, HH_DynaSand_v1).
Tertiary polishing of secondary effluent: up-flow filtration through a moving sand bed
with simultaneous airlift washing; wash water is a constant fraction (fWash) of influent
and leaves as a reject side-stream carrying the captured solids.
Built-in coagulant response: set Dose,alum (mg Al/L) or Dose,fe (mg Fe/L) > 0 to engage
alum / ferric chloride assistance (pilot-tested: alum 8-14, ferric 14-16 mg/L).
Calibrated to the Qaha
WWTP pilot: El-Gendy et al. 2026, Sustainability 18(12):6058, doi:10.3390/su18126058.
WASH ROUTING: Wash reject carries separated solids. Route it to an external reject outlet or a treatment path with net solids wasting. Returning all wash directly to this filter's inlet gives no net steady-state removal across the combined system.
COAGULANT DOSES are empirical capture modifiers: this unit does not calculate metal addition, hydroxide sludge generation or dosing-induced pH changes.

## Unit
Port | DynaSand connections
Symbol | Name | Position | Phase | Direction | Image | Size | Rule | Comments
inp | Influent | TL;;6px;12px | L | in | L | 24
eff | Filtrate | BR;;-6px;-12px | L | out | L | 24
wash | Wash water reject | TR;;-6px;12px | L | out | L | 24
Attribute | DynaSand attributes
Symbol | Name | Default | Rule | Comments
Volumeless | Volumeless point separator | TRUE | Constant
Input | Input process unit | FALSE | Hidden
InheritkinPAR | Kinetic parameter inheritance | FALSE | Inherit
InheritstoPAR | Stoichiometric parameter inheritance | TRUE | Inherit
InheritequPAR | Equilibrium parameter inheritance | TRUE | Inherit
Model | Models
Symbol | Name | Valid | Invalid | Rule | Comments
MODEL | Biokinetic model
Appearance | Unit appearance
Symbol | Name | Value | Rule
Default |  | HH_DynaSand_v1.emf
CustomSize |  | 174x90

## Parameters
Unit settings
Symbol | Name | Default | Low limit | High limit | Unit | Decimals | Rule | Principle/comment
fWash | Wash-water fraction of influent flow | 0.11 | 0.001 | 0.999 | - | 3
Diameter | Filter diameter | 0.96 | 0.05 |  | m | 3
BedDepth | Sand bed depth | 1.5 |  |  | m | 3
BedHeightEff | Effective bed height | 3.125 |  |  | m | 3
UnitHeight | Total unit height | 4.175 |  |  | m | 3
SandVolume | Sand inventory | 1.7 |  |  | m3 | 2
SandDmin | Media size (min) | 1.2 |  |  | mm | 2
SandDmax | Media size (max) | 2 |  |  | mm | 2
AirLiftQ | Air-lift air flow | 1.9 |  |  | m3/h | 2
fXTSS,rem | Base particulate concentration reduction (TSS proxy) | 0.621 | 0 | 1 | - | 3
fColloid,rem | Base colloidal concentration reduction (turbidity proxy, not direct NTU) | 0.67 | 0 | 1 | - | 3
fMaxTSS,alum | Alum max particulate concentration reduction | 0.717 | 0 | 1 | - | 3
fMaxTurb,alum | Alum max colloidal concentration reduction (turbidity proxy) | 0.945 | 0 | 1 | - | 3
fMaxTSS,fe | Ferric max particulate concentration reduction | 0.838 | 0 | 1 | - | 3
fMaxTurb,fe | Ferric max colloidal concentration reduction (turbidity proxy) | 0.814 | 0 | 1 | - | 3
KD,alum | Alum half-improvement dose | 7 | 0.001 | 100 | mg/L | 2
KD,fe | Ferric half-improvement dose | 7.5 | 0.001 | 100 | mg/L | 2
Dose,alum | Alum dose (mg Al/L; 0 = no coagulant) | 0 | 0 | 100 | mg/L | 2
Dose,fe | Ferric dose (mg Fe/L; 0 = no coagulant) | 0 | 0 | 100 | mg/L | 2

## Code
Model parameter inheritance
|  | Model parameters in outlets | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..PAR | MODEL.PAR.Name | Parent..PAR
| wash..PAR | MODEL.PAR.Name | Parent..PAR
Hydraulics
|  | Volumetric flows and loading | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..Q | Wash-water flow rate | inp..Q * fWash | m3/d
| eff..Q | Filtrate flow rate | inp..Q - wash..Q | m3/d
| BedArea | Filter bed cross-section | 3.14159265 * Diameter * Diameter / 4 | m2
| HLR | Hydraulic loading rate | inp..Q / BedArea | m/d
Coagulant response
|  | Effective removal fractions | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| fXTSS,eff | Effective particulate removal fraction | fXTSS,rem + (fMaxTSS,alum - fXTSS,rem) * Dose,alum / (KD,alum + Dose,alum) + (fMaxTSS,fe - fXTSS,rem) * Dose,fe / (KD,fe + Dose,fe) | - |  |  | bounded in [0,1] for single-coagulant dosing (parameter limits); simultaneous alum+ferric flagged by CoagConflict
| fCol,eff | Effective colloidal removal fraction | fColloid,rem + (fMaxTurb,alum - fColloid,rem) * Dose,alum / (KD,alum + Dose,alum) + (fMaxTurb,fe - fColloid,rem) * Dose,fe / (KD,fe + Dose,fe) | - |  |  | bounded in [0,1] for single-coagulant dosing (parameter limits); simultaneous alum+ferric flagged by CoagConflict
Effluent concentrations
|  | Filtrate concentrations | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..L.sSV | MODEL.SV.Name | inp..L.sSV
| eff..L.cSV | MODEL.SV.Name | inp..L.cSV * (1 - fCol,eff)
| eff..L.xSV | MODEL.SV.Name | inp..L.xSV * (1 - fXTSS,eff)
Calculated variables
|  | Stoichiometric calculated variables in filtrate | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..CVAR | MODEL.CVAR.Name | eff..MODEL.CVAR.Expression | MODEL.CVAR.Unit |  | Type(Stoichiometric)
|  | Stoichiometric calculated variables in wash water | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..CVAR | MODEL.CVAR.Name | wash..MODEL.CVAR.Expression | MODEL.CVAR.Unit |  | Type(Stoichiometric)
|  | Energy calculated variables in filtrate | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..CVAR | MODEL.CVAR.Name | eff..MODEL.CVAR.Expression | MODEL.CVAR.Unit |  | Type(Energy) | Carries T and TK onto the outlet; without this the downstream unit cannot resolve <pipe>..TK
|  | Energy calculated variables in wash water | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..CVAR | MODEL.CVAR.Name | wash..MODEL.CVAR.Expression | MODEL.CVAR.Unit |  | Type(Energy) | Carries T and TK onto the outlet; without this the downstream unit cannot resolve <pipe>..TK
Mass flows
|  | Filtrate and wash mass flows | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..F.L.sSV | MODEL.SV.Name mass flow | eff..Q * eff..L.sSV |  | 0
| eff..F.L.cSV | MODEL.SV.Name mass flow | eff..Q * eff..L.cSV |  | 0
| eff..F.L.xSV | MODEL.SV.Name mass flow | eff..Q * eff..L.xSV |  | 0
| eff..F.L.SV,molar | MODEL.SV.Name molar flow | eff..F.L.SV / AMP | mol P.d-1 | 0 | Only(SPO4)
| wash..F.L.sSV | MODEL.SV.Name mass flow | inp..F.L.sSV - eff..F.L.sSV |  | 0
| wash..F.L.cSV | MODEL.SV.Name mass flow | inp..F.L.cSV - eff..F.L.cSV |  | 0
| wash..F.L.xSV | MODEL.SV.Name mass flow | inp..F.L.xSV - eff..F.L.xSV |  | 0
| wash..F.L.SV,molar | MODEL.SV.Name molar flow | wash..F.L.SV / AMP | mol P.d-1 | 0 | Only(SPO4)
| wash..L.sSV | MODEL.SV.Name | inp..L.sSV |  |  |  | zero-flow-safe form (no division by wash..Q)
| wash..L.cSV | MODEL.SV.Name | inp..L.cSV * (1 + (1 - fWash) * fCol,eff / fWash) |  |  |  | zero-flow-safe form (no division by wash..Q)
| wash..L.xSV | MODEL.SV.Name | inp..L.xSV * (1 + (1 - fWash) * fXTSS,eff / fWash) |  |  |  | zero-flow-safe form (no division by wash..Q)
|  | Stoichiometric calculated variable mass flows in filtrate | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..F.CVAR | MODEL.CVAR.Name mass flow | eff..Q * eff..CVAR | MODEL.CVAR.Unit * m3.d-1 | 0 | Type(Stoichiometric)
|  | Stoichiometric calculated variable mass flows in wash water | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..F.CVAR | MODEL.CVAR.Name mass flow | wash..Q * wash..CVAR | MODEL.CVAR.Unit * m3.d-1 | 0 | Type(Stoichiometric)
pH mapping
|  | Equilibrium calculated variables in filtrate | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..CVAR | MODEL.CVAR.Name | inp..CVAR | MODEL.CVAR.Unit |  | pH; Type(Equilibrium) | Equilibrium calculated variables mapped from input port
|  | Equilibrium calculated variables in wash water | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..CVAR | MODEL.CVAR.Name | inp..CVAR | MODEL.CVAR.Unit |  | pH; Type(Equilibrium) | Equilibrium calculated variables mapped from input port
|  | Equilibrium species in filtrate | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..SPC | MODEL.Species.Name | inp..SPC | MODEL.Species.Unit |  | pH | Equilibrium species mapped from input port
|  | Equilibrium species in wash water | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..SPC | MODEL.Species.Name | inp..SPC | MODEL.Species.Unit |  | pH | Equilibrium species mapped from input port
|  | Charge balance and ionic strength in filtrate | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| eff..MODEL.pH.Symbol | MODEL.pH.Name | inp..MODEL.pH.Symbol | MODEL.pH.Unit |  | pH; Type(Chargebalance) | Charge balance and ionic strength mapped from input port
|  | Charge balance and ionic strength in wash water | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| wash..MODEL.pH.Symbol | MODEL.pH.Name | inp..MODEL.pH.Symbol | MODEL.pH.Unit |  | pH; Type(Chargebalance) | Charge balance and ionic strength mapped from input port
Diagnostics
|  | Local performance diagnostics (GUI) | Codelocation(Dynamic)
| Symbol | Name | Expression | Unit | Decimals | Rule | Principle/comment
| ReducTSS,loc | Local TSS concentration reduction | 1 - eff..XTSS / inp..XTSS | - | 3 |  | local to the unit; does not detect downstream wash recycling; unavailable when inlet TSS is zero
| DivertTSS,loc | Local TSS load diversion to wash | 1 - eff..Q * eff..XTSS / (inp..Q * inp..XTSS) | - | 3 |  | local to the unit; unavailable when inlet TSS or flow is zero
| ResidTSS | TSS balance residual | inp..Q * inp..XTSS - eff..Q * eff..XTSS - wash..Q * wash..XTSS | g.d-1 | 0 |  | should be ~0 at every operating point
| HLRh | Hydraulic loading rate | HLR / 24 | m/h | 2 |  | pilot tested range 3.9-8.5 m3/h feed (~5.4-11.7 m/h HLR)
| CoagConflict | Coagulant conflict (alum AND ferric both dosed) | Dose,alum * Dose,fe | - | 0 |  | nonzero = simultaneous alum+ferric (not pilot-validated; can push colloidal reduction above 1) - set one dose to 0

## Display
| Display variables | Location(Unit)
Symbol | Name | Value | Unit | Decimals | Rule | Principle/comment
inp..Q | Inlet flow rate |  | m3/d | 0
eff..Q | Filtrate flow rate |  | m3/d | 0
wash..Q | Wash reject flow rate |  | m3/d | 0
inp..XTSS | Inlet TSS |  | g.m-3 | 0
eff..XTSS | Filtrate TSS |  | g.m-3 | 0
wash..XTSS | Wash reject TSS |  | g.m-3 | 0
HLR | Hydraulic loading rate |  | m/d | 0

## Popup
| Popup variables | Location(Unit)
Symbol | Name | Value | Unit | Decimals | Rule | Principle/comment
inp..Q | Inlet flow rate |  | m3/d | 0
eff..Q | Filtrate flow rate |  | m3/d | 0
wash..Q | Wash reject flow rate |  | m3/d | 0
inp..XTSS | Inlet TSS |  | g.m-3 | 0
eff..XTSS | Filtrate TSS |  | g.m-3 | 0
wash..XTSS | Wash reject TSS |  | g.m-3 | 0
HLR | Hydraulic loading rate |  | m/d | 0
ReducTSS,loc | Local TSS concentration reduction |  | - | 3 |  | local; does not detect downstream wash recycling
DivertTSS,loc | Local TSS load diversion to wash |  | - | 3 |  | local
ResidTSS | TSS balance residual |  | g.d-1 | 0 |  | should be ~0
HLRh | Hydraulic loading rate |  | m/h | 2
CoagConflict | Coagulant conflict (alum AND ferric both dosed) |  | - | 0 |  | nonzero = set one dose to 0